A close up of a logo

Description automatically generated

**Addendum 10-12**

**Date: 6/5/2020**


**RFI Questions / Answers**

**10 Question: “**Does the Generator need to be fueled by the electrical contractor”

**Answer: “Yes** the electrical contractor is responsible for fueling of the generator throughout the testing process and topping it off before the turnover of the building.”

**11 Question:** "The bid package states to carry and allowance of $5000 for BIM in Plumbing, Mechanical, Electrical, and Fire Sprinkler while also requiring the trade to carry it in their number."

**Answer:** "Please remove the allowance of $5000. The Plumbing, Mechanical, Electrical, and Fire Sprinkler contractors should carry the cost of BIM coordination we supplied the names of 4 qualified companies/individuals to do this work"



**12 Question:** “Please advise if the above project will contain a Building Automation Systems (BAS) for the HVAC equipment."

**Answer:** "The VRF system type by default requires a certain amount of building automation.  It was intended by the engineer to only require what will be required by the system brand selected and to accomplish the limited sequence described in relation to the DOAS."