## Sheet1
RFI LOG
|  | DRAWING SET DATE: | 2026-05-29 | PROJECT NAME: |  | Flagship MOB II
|  |  |  | PROPOSAL #: |  | P25-1410-2
ITEM | SHEET | COMMENTS |  |  | RESP. | DESIGN RESPONSE
1 |  | Direct Digital controls (DDC) are specified for the HVAC system, but it is unusual to include DDC in the core & shell. Please confirm that a DDC system is to be included in the core & shell? |  |  |  | Controls are shown because VAV's are shown in the drawings. Provide controls as a breakout number.
2 |  | Please confirm if BIM is to be provided by the MEP contractors? |  |  |  | No.
3 |  | Will insulation be required behind spandrel glass as the details do not indicate this? |  |  | LS3P | No.
4 |  | Please provide direction on how to handle the door hardware for the storefront doors. The hardware specs calls for allowances to be carried for the door hardware but it doesn't specify who is to carry those allowances the GC or the trade partners. No hardware sets are listed in the specs or on the drawings. There's also a specification section for auto swing door operators but there is no direction on where those are required, how many and so forth. Please advise on how you want to approach of this portion of the project. |  |  | LS3P | Sub to carry allowance per HDW spec for doors shown in the drawings. LS3P please clarify which doors get door operators. LS3P is confirming with owner early next week.
5 |  | Who will be responsible for furnishing and installing the auto slide entrances? |  |  |  | Glazing Contractor
6 |  | Can you please verify the rough opening dimensions for the 1st and 2nd floor punched openings? The building elevations and section views show the first floor openings at 10’-0” inches high and the second level openings at 9’-4” high. The elevation drawings on A601 show all of the punched opening heights at 9’-4” with the exception of S7 that is shown at 10’-0”. |  |  |  | This is tilt panels so rough openings will be coordinated with window dimensions per A-601.
7 |  | Please confirm which trade package will be responsible for furnishing and installing the glass handrail system. |  |  |  | Glazing Contractor.
8 |  | Also with regard to the glass handrail system specification (057313-3, 2.1) calls for it to be a top mounted aluminum shoe based system with stainless steel top U and 1-1/2” diameter vertical tubes. The drawings however show the GH as a tube and post system with standoffs to attach the glass to. (ref. details on A-401 & A-701) Please clarify which is correct. |  |  | LS3P | It should match the specification. See attached for a typical section detail that will be included in the upcoming addendum.
9 |  | Can the raw output CPT data for the geotechnical borings be provided by TerraCon? This would be an excel file with the readings at each depth, because the graphical display in the report can be difficult to interpret. (Question for geotechnical engineer of record) |  |  | Terracon
10 |  | Can the structural engineer of record (SER) provide the actual gravity loads (Dead Loads and Live loads) for the individual column and wall foundations? This helps to optimize the design of ground improvement and often leads to less expensive estimates for support. This is most easily presented as a marked up version of the foundation plans. (Question for structural engineer of record) |  |  | Citadel
11 |  | Spec 084113-7 2.4 calls for thermal storefront doors. The framing systems for this project are not ultra thermal or dual thermal systems. Thermal doors work best with ultra thermal or dual thermal framing systems. Therefore will standard 1-3/4” aluminum storefront doors be acceptable instead of the thermal doors specified? |  |  | LS3P | Thermal storefront doors are specified to maintain continuity of the thermal barrier and to achieve the required assembly performance, including U-factor and air infiltration, per NFRC 100 and applicable energy code requirements. Standard 1-3/4" non-thermal aluminum storefront doors do not incorporate a thermal break and will result in increased conductive heat transfer and localized degradation of the fenestration system’s overall thermal performance. As such, they are not considered equivalent to the specified thermal doors. Substitution with non-thermal doors will only be considered upon submission of documented whole-assembly performance demonstrating compliance with specified U-factor, air infiltration criteria, and North Carolina Energy Conservation Code requirements. Approval is subject to Architect/Engineer review.
12 | LA-1 | What do the bright green areas shown in the parking lot islands represent? Sod, seed, mulch? Please clarify. |  |  | LS3P/CLD | LS3P defers to CLD.
13 |  | Door 105 has a note on the ext elev pgs. that says it should have a film, however there is also a note on the door schedule that says this should be a louvered door. Which is correct? |  |  | LS3P | This door should have a film (privacy film) and not be louvered.
14 | C1/A-202 | Is the film called out on the ext. elev pgs. only for the four elevations with arrows pointing to them? |  |  |  | Yes, only the four elevations.
15 | A-802 | Room Finish Schedule indicates that Stair A and Stair B are to receive PTF-1 flooring finish. Please clarify the intended placement of the tile. Is the PTF-1 tile to be installed on the stair landings only? |  |  | LS3P | We would like to revise Stair B to be Sealed Concrete finish on the landings (to match the risers) and would like Stair A to be PTF-1 on landings and treads.
16 | A-401 | A-401 indicates the use of rubber stair nosing. Please clarify the extent of the stair nosing installation. Are stair nosings required only at the top step/landing transitions, or are they to be installed on all stair treads throughout Stair A and Stair B? |  |  | LS3P | Rubber stair nosing should be on all stair treads on both stairs. Please account for two different profiles - Stair A should have a custom profile and Stair B can maintain a basic profile.
17 |  | Are we to include any mulch/pinestraw for the existing streetyard planting /trees? |  |  |  | Yes. We will get clarification as well
18 |  | Should we include sod outside of the LOD to the street corner for a new / complete look? I have attached our takeoff so you can see the areas outside of the LOD not included currently. |  |  |  | Yes. We will get clarification as well
19 |  | Will the underground wiring and site light poles be by the electrical contractor or Duke Power? |  |  |  | By Duke, but we will clarify
20 |  | There is not a location that identifies the electrical service entrance location. Will it possibly be by the electrical room close to the future generator? |  |  | LS3P | The final location will be determined in coordination with Duke Energy and is dependent on the Owner’s electrical service application. It is possible to provide a recommended service entrance location. However, the utility company will establish the final service point during their review process. Final location to be confirmed through coordination between DSA, the Contractor, and Duke Energy following service application.
21 |  | If the electrical service entrance location is by the electrical room, can CU-2 be moved to allow space to mount meter and CT cabinet? |  |  | LS3P/DSA | Yes, CU-2 can be relocated along the plan East exterior wall to avoid conflicts with incoming electrical service and associated meter/panel. Coordinate routing of refrigerant linesets and condensate drain piping to maintain required working clearance for electrical equipment.
22 |  | There is a reference to a time clock along with a photocell to control the lighting under the carport. I can find no other information on the type of time clock. Is the time clock required? If so, is there any additional information? |  |  | LS3P/DSA | Yes, time clock is required. Reference C405.2.5 In the North Carolina State Energy code for requirements.
23 |  | Are the HVAC controls rough-in by others than the EC? |  |  |  | Controls to be handled by the HVAC contractor, power to HVAC equipment is by electrical contractor.
24 |  | What size do the data stub-up's need to be? 3/4", 1" |  |  |  | Carry 3/4" and clarify in your proposal.
25 |  | There is not a location that identifies the data service entrance location. Is there a suggested location for take-off purposes? |  |  |  | Clarify service would come in the back of the building off Diligence Rd routing to IDF 102
26 |  | What are the approved Fire Alarm manufacturers other than Simplex? |  |  | LS3P/DSA | Approved alternates are Honeywell and Siemens - owner to confirm approved alternates
27 |  | Does the notifier system in this building need to be able to talk to the other at Novant Midtown? |  |  | LS3P | LS3P will be confirming with owner early next week.
28
29
30
31
32